{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["December Update"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":51,"comments":2,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"December Update","index":0,"n_rows":709,"n_cols":16,"rows_kept":709,"cut":false,"hidden":false,"merged":[]}
["ATCO-AUC-2021DEC31 - December 2021 Update"]
["Row No.","Location (LSD)","Class Location","Pipeline Size (mm)","Pipeline Name","Estimated No. Welds","MOP (kPa)","INSPECTED (Y/N)","ABOVE GROUND FIELD INSPECTION DATE","BELOW GROUND FIELD INSPECTION DATE","INSPECTION DISPOSITION","CRITICAL DEFECTS IDENTIFIED (Y/N)","DERATE PRESSURE (kPa)\n*pressure derates lifted once critical defects are repaired","DATE OF ENGINEERING ASSESSMENT","ASSESSMENT DISPOSITION","REPAIRS COMPLETE (Y/N)"]
[3,"LSD 12-19-27-24-W4",1,508,"Carbon Loop (508.0)",24,6240,"Y","2016-10-01","2016-10-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[4,"LSD 1-3-26-29-W4",1,508,"East Calgary B Extension",206,6240,"Y","2016-03-01","2016-03-01","Defects Found","Y",4000,"2016-12-01","Repairs Required","Y"]
[27,"12-19-054-27-W4",2,323,"Paddle River Transmission (CU Lease)",264,5520,"Y","2017-11-01","2019-06-01","Defects Found","Y","N/A","Not Started","Repairs Required","N"]
[47,"SW-04-52-24-W4M - NW-32-43-01-W5M","3,2,1",610,"Homeglen Transmission",304,6200,"Y","2016-03-01","N/A","Defects Found","Y",4535,"2017-08-01","Repairs Required","Y"]
[52,"NW-35-025-29-W4 &\nSW-02-026-29-W4",2,219,"Petrogas - Airdrie Transmission",184,5520,"Y","2016-03-01","2016-03-01","Defects Found","N","N/A","2016-12-01","Repairs Required","Y"]
[53,"NW-35-025-29-W4 &\nSW-02-026-29-W4",2,219,"Petrogas - Airdrie Transmission",23,5520,"Y","2016-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[79,"LSD 5-36-54-2-W5",2,219,"Paddle River Transmission",53,5520,"Y","2018-02-01","2018-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[105,"12-32-53-22-W4M",1,610,"Cloverbar Lateral",14,8450,"Y","2016-08-01","N/A","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[106,"1-4-55-20-W4M",1,610,"Cloverbar Lateral",14,8450,"Y","2016-08-01","2016-08-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[115,"LSD 5-26-27-25-W4",1,508,"Carbon Loop (508.0)",298,6240,"Y","2016-04-01","2016-04-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[116,"14-27-53-25-W4",1,508,"Northwest Edmonton Connector",420,3450,"Y","2016-06-01","2016-06-01","Defects Found","Y","N/A","2021-01-21","Repairs Required","Y"]
[117,"SE-21-53-23-W4",2,762,"Cloverbar Lateral",24,8450,"Y","2016-08-01","2016-08-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[118,"04-34-54-21 W4",2,610,"Cloverbar Lateral",35,8450,"Y","2016-08-01","2016-08-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[120,"16-24-51-25-W4 & 16-14-51-25-W4","3,1",114,"Bonnie Glen Transmission",5,6890,"Y","2017-01-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[123,"LSD 11-10-51-25-W5",3,88,"Jasper Transmission",15,6900,"Y","2017-01-01",null,"Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[124,"4-26-54-25-W4",3,273,"Bittern Lake Transmission",37,6580,"Y","2017-01-01","2019-04-01","Defects Found","N","N/A","2018-06-01","Repairs Required","Y"]
[125,"LSD 11-14-49-16-W4",3,60,"Viking-Edmonton Transmission - Line #3",24,4030,"Y","2017-11-01","2018-09-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[126,"NE-22-52-23-W4",3,168,"Viking 3 and 4",58,4960,"Y","2017-01-01","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[127,"6-34-50-26-W4",3,114,"Pine Valley Transmission",22,6895,"Y","2016-12-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[128,"SW-33-24-10-W5",3,168,"Banff Transmission",38,4960,"Y","2017-03-01","2018-10-01","Defects Found","N","N/A","2020-02-01","Repairs Required","N"]
[129,"LSD-11-8-52-24-W4M",3,168,"Rossdale Transmission",24,2070,"Y","2017-01-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[130,"SE-5-25-10-W5",3,168,"Banff Transmission",34,4960,"Y","2017-03-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[131,"4-32-51-24-W4",3,26,"Swan Hills Transmission",6,4030,"N",null,"N/A"]
[132,"16-5-30-1-W5",3,88,"Airdire - Penhold Transmission",16,4960,"Y","2017-05-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[133,"04-04-054-18-W4",1,508,"Inland-Ft Saskatchewan Transmission",18,8450,"Y","2017-05-01","2018-03-01","Defects Found","N","N/A","2018-06-01","Repairs Required","N"]
[134,"16-24-052-17-W4",1,508,"Inland-Ft Saskatchewan Transmission",25,8450,"Y","2017-02-01","2018-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[135,"16-34-050-15-W4",1,508,"Inland-Ft Saskatchewan Transmission",23,8450,"Y","2017-02-01","2018-03-01","Defects Found","N","N/A","2018-06-01","Repairs Required","Y"]
[136,"15-19-52-25-W4",3,114,"Swan Hills Transmission",44,6205,"Y","2017-01-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[137,"LSD 9-19-23-1-W5",3,323,"Jumping Pound Transmission",33,4960,"Y","2016-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[138,"16-24-052-17-W4",1,508,"Inland-Ft Saskatchewan Transmission",100,8450,"Y","2017-03-01","2018-03-01","Defects Found","N","N/A","2018-08-01","No Repairs Required","N/A"]
[139," NE-21-023-01-W5",3,323,"Jumping Pound Transmission",49,4960,"Y","2016-12-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[140,"NW 1/4-23-22-1-W5M",3,323,"Priddis Transmission Line (406.3)",26,6140,"Y","2016-12-01","N/A","Defects Found","N","N/A","2018-09-01","No Repairs Required","N/A"]
[141,"NW-23-22-1-W5",3,406,"Priddis Transmission Line (406.3)",50,4960,"Y","2016-12-01","2017-10-01","Defects Found","N","N/A","2018-05-01","No Repairs Required","N/A"]
[142,"LSD 9-22-23-1-W5",3,323,"Jumping Pound Transmission",43,4960,"Y","2016-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[143,"9-22-23-1-W5M",3,406,"Mainline",21,4960,"Y","2016-12-01","2016-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[144,"SE-27-23-1-W5",3,273,"Mainline Loop #1",4,3020,"Y","N/A","2016-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[145,"04-01-053-28-W4","2,1",168,"Stony Plain Transmission",84,3450,"Y","2017-01-01","2017-01-01","Defects Found","N","N/A","2018-02-01","No Repairs Required","N/A"]
[146,"09-22-23-1-W5 & NE-21-23-29-W4","3,2",323,"Jumping Pound Transmission",16,4960,"Y","N/A","2016-12-01","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[148,"LSD 8-23-34-1-W5",3,168,"Nevis - Airdrie",37,4960,"Y","2017-06-01","N/A","Defects Found","Y",3600,"Not Started","Repairs Required","Y"]
[149,"LSD 14-14-23-27-W4 - LSD 4-4-23-28-W4","3,1",114,"Indus Lateral",115,6240,"Y","2017-02-01","2018-12-01","Defects Found","N","N/A","2021-01-21","No Repairs Required","N/A"]
[150,"14-30-24-2-W5 to 6-31-24-2-W5","3,2",168,"Valley Ridge Branch",54,4960,"Y","2017-08-01","2020-02-01","Defects Found","N","N/A","2021-01-21","No Repairs Required","N/A"]
[151,"NW/SW-6-54-16-W4",1,508,"Norma Transmission",9,8450,"Y","2017-03-01","2018-02-01","Defects Found","N","N/A","2018-06-01","No Repairs Required","N/A"]
[152,"4-19-53-23-W4 to 8-7-53-23-W4",3,323,"Hermitage Transmission",2,6450,"N","N/A"]
[153,"SE-30-051-24-W4 ",3,114,"Pembina Transmission",6,6140,"Y","N/A","2018-07-01","Defects Found","N","N/A","2020-06-20","No Repairs Required","N/A"]
[154,"SE-21-53-23-W4",2,610,"SEEP",153,8450,"Y","2017-08-01","2017-08-01","Defects Found","Y","Isolated","Not Required","Repairs Required","Y"]
[155,"NW-4-41-26-W4 ",1,219,"Southern Extension",21,4830,"Y","2017-06-01","2020-05-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[156,"LSD 2-27-38-27-W4",3,168,"Southern Extension",3,4830,"N","N/A"]
[157,"E(1/2) 14-24-2-W5",3,406,"North Line Branch",55,4960,"Y","2017-03-01","2021-03-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[158,"E (1/2) 29-22-29-W4",3,219,"McKenzie Gate Lateral",45,6140,"Y","2017-08-01","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[159,"NW-10-41-26-W4",1,219,"Southern Extension",28,4830,"Y","2018-01-01","2020-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[161,"LSD 2-25-24-2-W5",3,273,"North Branch Line",29,4960,"Y","2017-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[162,"7-17-25-1-W5",3,406,"Jumping Pound West Transmission",45,5090,"Y","2017-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[163,"12-33-55-21W4 &\n13-33-55-21W4 & \n12-08-56-21W4",2,610,"Esso Chemical Lateral",133,8450,"Y","2017-11-01","2021-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[164,"4-34-53-18-W4",1,508,"Norma Transmission",263,8450,"Y","2017-03-01","2018-02-01","Defects Found","Y",5790,"2018-07-01","Repairs Required - \nCritical Defects Repaired","Y"]
[166,"SE-02-42-26-W4",3,219,"Southern Extension",53,4830,"Y","2018-08-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[167,"SE-13-27-1-W5",3,219,"Petrogas - Airdrie Transmission",8,4960,"Y","N/A","2019-07-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[168,"SE-13-42-26-W4",1,219,"Southern Extension",68,4830,"Y","2018-03-01","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[170,"SE-13-42-26-W4",1,219,"Southern Extension",31,4830,"Y","2017-03-01","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[171,"LSD 13-14-53-25-W4",3,60,"North Edmonton Loop",123,3450,"Y","2017-03-01","2019-07-01","Defects Found","N","N/A","2020-03-01","No Repairs Required","N/A"]
[172,"NE-19-42-25-W4",1,219,"Southern Extension",35,4830,"Y","2018-01-01","2020-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[173,"SE-30-42-25-W4",1,219,"Southern Extension",38,4830,"Y","2017-12-01","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[174,"LSD 9-28-48-26-W4",1,60,"Millet Transmission",59,6200,"Y","2017-03-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[175,"SW-15-43-25-W4",1,219,"Southern Extension",37,4830,"Y","2017-06-01","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[176,"SW-22-43-25-W4",1,219,"Southern Extension",72,4830,"Y","2017-11-01","2021-02-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[177,"SE-1-54-25-W4",3,508,"North Edmonton Loop",64,3450,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[178,"LSD 1-23-51-25-W5",2,114,"Jasper Transmission",82,6900,"Y","2017-07-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[179,"NW-26-43-25-W4",1,219,"Southern Extension",35,4830,"Y","2017-09-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[180,"16-6-49-27-W5",2,60,"Jasper Transmission",12,6205,"Y","2017-03-01","2020-04-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[181,"SW-12-44-25-W4",1,219,"Southern Extension",17,4830,"Y","2017-06-01","2020-04-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[182,"SW-03-45-24-W4",1,219,"Southern Extension",22,4830,"Y","2017-12-01","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[183,"NE-29-45-23-W4",1,219,"Southern Extension",67,4830,"Y","2017-09-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[184,"NE-27-050-26-W4",2,219,"Devon Transmission",14,6890,"Y","2018-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[185,"SE-10-46-23-W4",1,219,"Southern Extension",62,4830,"Y","2017-08-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[186,"SE-27-46-22-W4",1,219,"Southern Extension",165,4830,"Y","2018-02-01","2020-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[188,"LSD 2-3-55-22-W4",2,219,"Bittern Lake to Redwater transmission",223,4960,"Y","2018-03-01","2019-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[190,"13-19-54-25-W4",2,88,"Paddle River Transmission",4,5520,"Y","2017-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[191,"9-7-52-6-W5",2,60,"Wabamun to Hinton Transmission",16,7240,"Y","2018-03-01","N/A","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[192,"LSD 8-17-50-7-W5",2,60,"Pembina Lobstick Transmission",13,8274,"Y","2017-04-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[193,"3-8-49-7-W5",2,60,"Pembina Lobstick Transmission",20,3720,"Y","2018-03-01","2018-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[194,"LSD 15-12-28-26-W4",2,60,"Acme Lateral",13,5515,"Y","2017-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[195,"NW-29-46-21-W4",1,219,"Southern Extension",53,4830,"Y","2018-02-01","2020-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[196,"1-4-49-26-W4",1,610,"Homeglen Transmission",10,6200,"Y","N/A","2017-08-01","Defects Found","N","N/A","2018-06-01","Repairs Required","Y"]
[197,"11-13-26-27-W4M",2,406,"Carbon Transmission",64,5520,"Y","2017-03-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[198,"8-17-29-22-W4 & SW 16-29-22-W4M",2,406,"Carbon Transmission",13,5520,"Y","2017-08-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[199,"LSD 15-23-053-17-W5",2,60,"Wabamun to Hinton Transmission",14,7240,"Y","2019-03-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[200,"LSD 4-27-51-25-W4",2,114,"Golden Spike Transmission",41,6200,"Y","2017-03-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[201,"SW-31-52-23-W4",2,88,"East Edmonton Interconnection",61,6450,"Y","2018-06-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[202,"4-24-25-1-W5",2,219,"Jumping Pound West Transmission",46,5090,"Y","2017-03-01","2019-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[203,"1-23-024-03-W5",2,323,"Jumping Pound Transmission",20,4960,"Y","2017-05-01","2019-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[204,"5-18-25-2-W5",2,60,"Jumping Pound West Transmission",8,5090,"Y","2017-03-01","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[205,"SW-16-53-23-W4",2,60,"Cloverbar Lateral",20,8450,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[206,"LSD-2-17-14-18-W4M",2,60,"Enchant Branch",9,6620,"Y","2017-08-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[207,"LSD-2-21-53-23-W4M",2,323,"Villeneuve Transmission",2,8450,"Y","2017-05-01","N/A","Defects Found","Y","Isolated","Not Required","Repairs Required","Y"]
[208,"5-10-55-22-W4",2,323,"Legal-Uncas Transmission",39,3447,"Y","2018-04-01","2018-05-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[209,"NE-22-42-2-W5M",2,60,"Rimbey Nova South Transmission",11,6200,"N","N/A"]
[210,"LSD 1-12-56-22-W4M",2,168,"Redwater Transmission",79,4960,"Y","2017-10-01","2021-08-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[211,"LSD 4-10-53-26-W4",2,114,"Swan Hills Transmission",36,6380,"Y","2017-09-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[212,"2-18-32-1-W5",2,323,"Olds Receipt Transmission",48,4960,"Y","2018-01-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[213,"SE-3-26-4-W5",2,168,"Cochrane Branch",26,4960,"Y","2017-03-01","2021-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[214,"5-10-55-22-W4",2,114,"Legal-Uncas Transmission",16,3447,"Y","2017-12-01","N/A","Defects Found","N","N/A","2018-05-01","No Repairs Required","N/A"]
[215,"LSD 4-10-53-26-W4",2,114,"Swan Hills Transmission",23,6380,"Y","2017-11-01","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[216,"NE-25-44-7-W4",2,114,"Wainwright Transmission",122,1900,"Y","2018-04-01","2018-11-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[217,"9-2-50-1-W4",2,114,"Lloydminster Transmission",55,5520,"Y","2017-10-01","N/A","Defects Found","N","N/A","2020-08-20","No Repairs Required","N/A"]
[219,"LSD-6-31-55-21-W4M",2,219,"Air Products Delivery Lateral",102,4960,"Y","2018-05-01","2019-10-01","Defects Found","N","N/A","2020-02-01","No Repairs Required","N/A"]
[220,"SE-17-053-26-W4",2,323,"Swan Hills Transmission",10,6380,"Y","2017-08-01","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[221,"SE-17-29-22-W4",2,273,"Carbon Transmission",57,5515,"Y","2017-08-01","N/A","Defects Found","N","N/A","2020-02-01","No Repairs Required","N/A"]
[222,"NE-05-053-23-W4",2,219,"East Edmonton Interconnection",21,4960,"Y","2018-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[223,"LSD 9-14-55-22-W4",2,60,"Bittern Lake Transmission",98,4960,"Y","2018-02-01","2019-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[224,"SE-8-53-23-W4",2,219,"East Edmonton Interconnection",64,8450,"Y","2018-05-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[225,"SE-21-53-23-W4",2,219,"Cloverbar Compressor",67,8450,"Y","2017-09-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[226,"LSD 9-4-25-28-W4",2,88,"Carbon Transmission",18,5520,"Y","2017-08-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[227,"LSD 16-36-51-4-W5",2,219,"Genesee-Keephills Transmission",226,4960,"Y","2018-02-01","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[228,"LSD 10-30-72-4-W5",2,114,"Mitsue Plywood",155,1730,"Y","2018-08-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[229,"LSD-3-14-55-22-W4M",2,114,"Bittern Lake to Redwater transmission",41,4960,"Y","2018-02-01","2019-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[230,"8-21-53-25-W4",2,114,"North Edmonton Loop",31,3450,"Y","2017-10-01","2019-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[231,"4-33-54-22-W4",2,114,"Legal-Uncas Transmission",23,4450,"Y","2017-12-01","2019-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[232,"SE-19-049-24-W4",2,323,"Usona Transmission",40,7660,"Y","2017-12-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[233,"NW-17-056-21-W4",2,273,"Bittern Lake to Redwater Transmission",152,4830,"Y","2018-05-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[234,"LSD 4-4-22-29-W4",2,114,"Dewinton East Branch #1",15,2070,"Y","2017-09-01","2019-02-01","Defects Found","N","N/A","2020-10-01","No Repairs Required","N/A"]
[235,"NW-22-024-10-W5",3,323,"Banff Loop (323.9)",30,4960,"Y","2017-03-01","2018-10-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[236,"12-23-49-1-W5 to 12-14-49-1-W5",1,88,"Thorsby Lateral",164,6140,"Y","2017-11-01","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[237,"SE-7-25-10-W5 to SE-28-24-10-W5",1,323,"Banff Loop (323.9)",98,4960,"Y","2017-05-01","2018-11-01","Defects Found","N","N/A","2019-02-01","No Repairs Required","N/A"]
[238,"7-18-56-21-W4M",2,60,"Redwater Transmission",131,4960,"Y","2018-05-01","2020-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[239,"LSD 2-3-55-22-W4",2,219,"Bittern Lake to Redwater transmission",193,4960,"Y","2018-03-01","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[240,"NE-14-055-22-W4",2,168,"Bittern Lake to Redwater transmission",153,4960,"Y","2018-03-01","2019-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[241,"LSD 15-30-72-4-W5",2,60,"Mitsue Plywood",3,1730,"Y","2018-08-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[242,"13-6-57-8-W5",2,273,"Paddle River Transmission",75,5520,"Y","2017-02-01","2018-04-01","Defects Found","N","N/A","2018-02-01","No Repairs Required","N/A"]
[243,"LSD 12-21-52-23-W5",1,60,"Wabamun to Hinton Transmission",98,7240,"Y","2017-07-01","N/A","Defects Found","N","N/A","2018-08-01","No Repairs Required","N/A"]
[244,"4-19-15-21-W4",1,273,"Champion Transmission",43,6740,"Y","2017-06-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[245,"7-15-25-4-W5",1,323,"Jumping Pound Transmission",171,4960,"Y","2017-05-01","2021-02-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[246,"03-10-055-22-W4",2,323,"Legal-Uncas Transmission",173,3447,"Y","2018-03-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[247,"NE-22-023-01-W5",3,406,"Jumping Pound Transmission",33,4960,"Y","2017-05-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[248,"10-10-55-22-W4",2,323,"Legal-Uncas Transmission",47,4960,"Y","2018-04-01","2021-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[249,"7-17-47-27-W4",1,610,"Homeglen Transmission",6,6205,"Y","N/A","2017-08-01","Defects Found","N","N/A","2018-06-01","Repairs Required","Y"]
[250,"LSD 4-5-44-1-W5",1,610,"Homeglen Transmission",3,6200,"Y","N/A","2017-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[251,"LSD 3-27-44-1-W5",1,610,"Homeglen Transmission",2,6200,"Y","N/A","2017-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[252,"SW-10-051-25-W4",1,610,"Homeglen Transmission",2,6890,"Y","N/A","2017-10-01","Defects Found","N","N/A","2018-08-01","No Repairs Required","N/A"]
[253,"LSD 4-3-55-22-W4",2,219,"Legal-Uncas Transmission",301,4140,"Y","2018-05-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[254,"1-2-24-2-W5",3,406,"North Branch Line",25,4960,"Y","2017-06-01","2020-10-01","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[255,"12-19-27-24-W4",1,88,"Carbon Transmission",60,6240,"Y","2017-11-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[256,"NE-16-053-23-W4",1,508,"East Edmonton Interconnection",68,3100,"N","N/A"]
[257,"NE-16-053-23-W4",1,508,"East Edmonton Interconnection",48,3100,"N","N/A"]
[258,"SE-26-052-24-W4",3,323,"Viking-Edmonton Transmission - Line #4",332,3447,"Y","2017-11-01","2018-03-01","Defects Found","N","N/A","2019-12-01","Repairs Required","Y"]
[259,"NW-34-038-01-W5",3,114,"Sylvan Lake Transmission",16,4690,"Y","2017-06-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[260,"LSD 12-3-10-23-W4",1,406,"Mainline East (West)",293,4960,"Y","2017-11-01","2020-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[261,"NE-24-052-23-W4",3,323,"Bretona Transmission",97,4960,"Y","2018-02-01","2018-05-01","Defects Found","N","N/A","2020-01-01","Repairs Required","Y"]
[262,"05-27-035-28-W4",2,168,"Nevis - Airdrie",72,4960,"Y","2017-07-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[263,"13-15-50-10-W4",1,273,"Birch Lake Transmission",85,8450,"Y","2017-12-01","2018-06-01","Defects Found","N","N/A","2018-03-01","Repairs Required","N"]
[264,"SW-02-47-21-W4",1,219,"Southern Extension",21,4830,"Y","2018-09-01","2020-03-20","Defects Found","N","N/A","Not Started ","Unknown","N"]
[268,"11-08-052-24-W4",4,323,"Rossdale Transmission",25,2070,"Y","2017-11-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[269,"SE-10-055-22-W4",2,60,"Legal-Uncas Transmission",4,3450,"Y","2018-04-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[270,"SW-05-056-21-W4",2,60,"Scotford Upgrader Expansion 1 Transmission",673,8450,"Y","2018-05-01","2021-09-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[272,"16-36-48-13-W4M",1,406,"Viking-Edmonton Transmission - Line #3",58,4030,"Y","2017-12-01","2018-10-01","Defects Found","N","N/A","2019-04-01","Repairs Required","Y"]
[273," SE-07-47-20-W4",1,219,"Southern Extension",13,4830,"Y","2018-03-01","2020-04-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[274,"LSD 16-6-20-25-W4",1,219,"Arrowwood Transmission",29,6620,"Y","2017-12-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[275,"SE-34-55-21-W4 TO\nSW-05-56-21-W4","2,1",406,"Scotford Upgrader Expansion 1 Transmission",49,8450,"Y","2018-05-01","2021-09-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[276,"12-3-56-21-W4",1,114,"Esso Chemical Lateral",38,8450,"Y","2018-01-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[277,"NW-25-19-29-W4",1,60,"Mainline East (West)",76,4960,"Y","2017-06-01","2020-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[279,"LSD-2-4-10-15-W4M",1,88,"Fincastle South Transmission",79,4965,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[280,"LSD 7-36-56-7-W5",1,273,"Paddle River Transmission",36,5520,"Y","2018-02-01","2017-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[281,"SW-02-026-29-W4",2,88,"Petrogas - Airdrie Transmission",17,4960,"Y","2017-09-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[282,"SE-14-52-8-W4",1,168,"Myrnam Transmission",24,8450,"Y","2017-09-01","2018-06-01","Defects Found","N","N/A","2018-06-01","No Repairs Required","N/A"]
[283,"LSD 5-13-52-8-W4",1,168,"Myrnam Transmission",34,8270,"Y","2017-09-01","2018-06-01","Defects Found","N","N/A","2018-07-01","Repairs Required","N"]
[284,"LSD 5-2-48-8-W5",1,60,"Pembina Transmission",18,6580,"Y","2017-10-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[285,"LSD 5-2-48-8-W5",1,33,"Pembina Transmission",20,6580,"Y","2017-09-01","2018-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[286,"15-36-12-27-W4",1,114,"Claresholm - N.E. Transmission",39,4960,"Y","2017-06-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[287,"14-14-023-27-W4",3,60,"Indus Lateral",2,6240,"Y","2017-08-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[288,"5-31-56-6-W5",1,273,"Paddle River Transmission",67,5520,"Y","2017-09-01","2018-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[289,"LSD 8-36-56-7-W5",1,273,"Paddle River Transmission",11,5520,"Y","2017-08-01","2018-06-01","Defects Found","N","N/A","2018-10-01","No Repairs Required","N/A"]
[290,"12-20-55-3-W5",1,323,"Paddle River Transmission",20,5520,"Y","2017-10-01","2018-07-01","Defects Found","N","N/A","2018-10-01","No Repairs Required","N/A"]
[291,"SW-28-25-05-W5",1,33,"Banff Transmission",3,4960,"Y","2017-06-01","N/A","Defects Found","N","N/A","2019-02-01","No Repairs Required","N/A"]
[292,"2-4-25-8-W5 to \n3-4-25-8-W5",1,219,"Banff Transmission",20,4960,"Y","2020-09-01","2018-10-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[293,"15-14-24-9-W5",1,60,"Banff Loop (323.9)",12,4960,"Y","2017-06-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[294,"01-05-53-26-W4",2,60,"Stony Plain Transmission",9,3450,"Y","2018-03-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[295,"3-8-54-26-W4 & 8-5-54-26-W4",1,273,"Paddle River Transmission",39,5520,"Y","2017-11-01","2018-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[296,"9-36-54-24-W4",1,323,"Bittern Lake to Redwater transmission",43,4140,"Y","2017-09-01","2020-03-01","Defects Found","N","N/A","2019-01-01","No Repairs Required","N/A"]
[297,"SW-10-47-20-W4",1,219,"Southern Extension",92,4830,"Y","2018-01-01","2020-07-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[298,"10-8-56-21-W4",1,168,"Bittern Lake to Redwater transmission",54,8450,"Y","2017-11-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[299,"06-29-051-24-W4",3,114,"Pembina Transmission",19,6140,"Y","2017-09-01","N/A","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[300,"12-1-56-5-W5",1,323,"Paddle River Transmission",38,5520,"Y","2017-11-01","2018-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[301,"02-14-25-28-W4",1,406,"Carbon Transmission",52,5520,"Y","2017-06-01","2018-11-01","Defects Found","N","N/A","2021-01-21","No Repairs Required","N/A"]
[302,"02-14-25-28-W4",1,406,"Carbon Transmission",4,5520,"Y","N/A","2016-08-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[303,"SW-35-059-12-W5",3,219,"Whitecourt Transmission",40,6210,"Y","2017-10-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[304,"LSD 8-31-38-28-W4",1,88,"Sylvan Lake Transmission",5,4688,"N",null,"N/A"]
[305,"LSD 13-13-25-5-W5",1,323,"Jumping Pound West Transmission",32,5090,"Y","2017-12-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[306,"SE-36-052-23-W4",3,273,"Bittern Lake to Redwater transmission",20,6830,"Y","2017-12-01","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[307,"11-12-54-26-W4M",1,323,"Villeneuve Transmission",6,8480,"Y","2017-11-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[308,"SW-03-025-04-W5",1,60,"Jumping Pound Transmission",16,4960,"Y","2017-08-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[309,"13-4-55-22-W4",1,273,"Bittern Lake to Redwater Transmission",24,4140,"Y","2018-02-01","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[310,"NE-11-039-27-W4",2,88,"Blackfalds Industrial Branch",9,4820,"Y","2017-08-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[311,"SE-06-049-14-W4",1,406,"Viking-Edmonton Transmission - Line #3",73,4030,"Y","2018-02-01","2018-09-01","Defects Found","N","N/A","2019-11-01","Repairs Required","Y"]
[312,"NE-35-023-02-W5",1,323,"Jumping Pound Transmission",10,4960,"Y","2017-09-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[313,"SE-03-053-26-W4",2,273,"Swan Hills Transmission",41,6200,"Y","2018-01-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[314,"LSD 5-30-9-25-W4",1,88,"Fort Macleod Branch",12,2070,"Y","2017-08-01","N/A","Defects Found","N","N/A","2018-03-01","No Repairs Required","N/A"]
[315,"5-15-49-2-W5",1,88,"Pembina Transmission",92,6140,"Y","2017-11-01","2018-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[316,"11-03-053-26-W4",2,323,"Swan Hills Transmission",28,6380,"Y","2018-03-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[317,"5-8-49-15-W4M",1,406,"Viking-Edmonton Transmission - Line #3 / Line #4",70,4030,"Y","2017-12-01","2018-11-01","Defects Found","N","N/A","2019-11-01","No Repairs Required","N/A"]
[318,"LSD 3-33-48-8-W5",1,88,"Pembina Transmission",11,6580,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[319,"03-30-024-28-W4",2,406,"Rockyview Branch",114,5090,"Y","2019-08-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[320,"NE-10-47-20-W4",2,219,"Southern Extension",43,4830,"Y","2017-08-01","2020-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[321,"SW-27-49-1-W5",1,114,"Pembina Transmission",66,6140,"Y","2017-10-01","2018-07-01","Defects Found","N","N/A","2020-06-20","No Repairs Required","N/A"]
[322,"LSD 8-33-9-22-W4",1,219,"Lethbridge Power Plant Lateral",12,2070,"Y","2017-08-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[323,"04-06-054-23-W4",2,219,"Fort Sask North Edmonton Lateral",124,3450,"Y","2017-11-01","2019-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[324,"16-33-010-21-W4",3,60,"Picture Butte Branch",8,2070,"Y","2017-10-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[325,"02-11-054-24-W4",3,406,"Villeneuve Transmission",14,8480,"Y","2018-02-01","2018-05-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[326,"1-3-51-25-W4 to 10-27-50-25-W4",1,219,"Nisku Lateral",189,6140,"Y","2018-02-01","2018-09-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[327,"3-5-28-24-W4",1,406,"Carbon Transmission",40,5520,"Y","2017-09-01","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[328,"16-15-49-16-W4M",1,406,"Viking-Edmonton Transmission - Line #3 / Line #4",100,4030,"Y","2017-10-01","2018-10-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[329,"4-23-25-29-W4",1,406,"Petrogas - Meadowfield Transmission",33,4960,"Y","2017-09-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[330,"LSD 9-36-50-19-W4M",1,406,"Viking-Edmonton Transmission - Line #3",95,4030,"Y","2018-01-01","2018-10-01","Defects Found","N","N/A","2019-04-01","Repairs Required","Y"]
[331,"1-24-53-6-W5",1,273,"Wabamun to Hinton Transmission",57,7240,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[332,"LSD 13-16-27-25-W4",1,406,"Carbon Transmission",53,6240,"Y","2017-09-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[333,"16-19-52-21-W4",1,406,"Viking-Edmonton Transmission - Line #3 / Line #4",149,4030,"Y","2017-11-01","2018-08-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[335,"04-30-024-28-W4",2,406,"Rockyview Branch",154,5090,"Y","2017-11-01","2019-09-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[336,"14-28-037-27-W4",2,114,"Nevis - Airdrie",15,4960,"Y","2017-08-01","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[337,"09-29-022-29-W4",3,219,"McKenzie Gate Lateral",9,6140,"Y","2017-08-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[338,"LSD 16-35-34-25-W4",1,88,"Trochu Transmission",45,6620,"Y","2017-12-01","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[339,"3-1-49-13-W4M to 16-20-49-16-W4M",1,26,"Viking-Edmonton Transmission - Line #3 / Line #4",126,8460,"Y","2018-09-01","N/A","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[340,"08-01-054-25-W4",3,406,"North Edmonton Loop",4,3450,"Y","N/A","2021-03-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[341,"1-1-38-27-W4",1,219,"Nevis - Airdrie",221,4960,"Y","2018-01-01","2018-10-01","Defects Found","N","N/A","2018-08-01","Repairs Required","Y"]
[342,"NW-08-053-23-W4 ",2,88,"East Edmonton Interconnection",18,3450,"Y","2017-08-01","2019-06-01","Defects Found","N","N/A","2019-09-01","No Repairs Required","N/A"]
[343,"SE-26-028-01-W5",3,60,"Nevis - Airdrie",12,4960,"Y","2017-11-01","2019-04-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[344,"SE-21-21-29-W4 to SW-20-21-28-W4","2,1",88,"Dewinton East Branch #2",22,2070,"Y","2017-06-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[345,"LSD 3-2-27-26-W4",1,406,"Carbon Transmission",43,5515,"Y","2017-09-01","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[346,"LSD 16-10-51-21-W4M",1,26,"Viking-Edmonton - Loops & Branches",13,2410,"Y","2017-12-01","2018-09-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[347,"10-15-51-12-W4",1,60,"Lavoy-Minburn Transmission",29,3450,"Y","2017-09-01","2018-06-01","Defects Found","N","N/A","2019-01-01","No Repairs Required","N/A"]
[348,"11-22-53-8-W5",1,273,"Wabamun to Hinton Transmission",11,7240,"Y","2018-10-01","2018-10-01","Defects Found","N","N/A","2020-10-01","No Repairs Required","N/A"]
[349,"LSD-16-36-48-13-W4M",1,323,"Birch Lake Transmission",20,8450,"Y","2017-11-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[350,"LSD 10-33-51-23-W4",1,26,"Bretona Transmission",11,4960,"Y","2017-12-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[351,"12-21-038-27-W4",3,168,"Nevis Transmission",91,4960,"Y","2018-01-01",null,"Defects Found","N","N/A","2021-01-21","No Repairs Required","N/A"]
[352,"1-18-53-21-W4M",1,168,"Legal-Uncas Transmission",5,3450,"Y","2017-08-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[353,"SW-22-43-25-W4",1,219,"Wood River Lateral",5,4830,"N",null,"N/A"]
[354,"LSD 7-15-88-9-W4",1,88,"Fort McMurray Transmission",25,6210,"Y","2016-10-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[355,"NW 1/4-23-22-2-W5M",1,406,"Priddis Transmission Line (406.3)",7,6140,"Y","2017-09-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[356,"1-6-38-25-W4M",1,219,"Nevis - Airdrie",43,4960,"Y","2018-03-01","2018-10-01","Defects Found","N","N/A","2018-06-01","No Repairs Required","N/A"]
[357,"LSD 9-12-46-20-W4",1,60,"Nevis - Airdrie",46,8450,"Y","2018-03-01","2020-10-01","Defects Found","N","N/A","2019-02-01","No Repairs Required","N/A"]
[358,"1-4-55-20-W4",1,406,"Inland Transmission",22,8450,"Y","2017-06-01","N/A","Defects Found","Y","Isolated","2018-06-01","Repairs Required","Y"]
[359,"LSD 3-2-20-29-W4",1,219,"Arrowwood Transmission",16,6620,"Y","2017-09-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[360,"1-28-53-9-W5M",1,219,"Wildwood Lateral",29,9930,"Y","2017-11-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[361,"LSD 5-19-50-5-W4",1,323,"Ranfurly Transmission",26,8270,"Y","2018-01-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[362,"LSD-16-29-48-9-W5M",1,88,"Pembina Transmission",17,6580,"Y","2018-03-01","N/A","Defects Found","N","N/A","2019-09-01","No Repairs Required","N/A"]
[363,"LSD-1-6-54-21-W4M",1,323,"Inland-Ft Saskatchewan Transmission",115,8450,"Y","2018-03-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[364,"NE-34-049-17-W4",1,406,"Viking-Edmonton Transmission - Line #3 / Line #4",169,4030,"Y","2017-11-01","2018-10-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[365,"1-4-52-20-W4",1,406,"Viking-Edmonton Transmission - Line #3 / Line #4",85,4030,"Y","2017-11-01","2018-08-01","Defects Found","N","N/A","2020-01-01","No Repairs Required","N/A"]
[366,"LSD 14-16-53-23-W4M",1,323,"Ardrossan Transmission",33,3100,"Y","2017-09-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[367,"1-22-35-11-W4",1,88,"Coronation Town Line",11,6210,"Y","2017-12-01","2020-10-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[368,"LSD 16-27-48-9-W5",1,114,"IS5053",11,6580,"Y","2017-12-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[369,"SE-28-50-9-W4",1,323,"Birch Lake Transmission",22,8450,"Y","2017-06-01","2017-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[370,"LSD 1-2-20-28-W4",1,219,"Arrowwood Transmission / Mazeppa-Canoxy Transmission",6,6620,"Y","2017-06-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[371,"NE-19-47-19-W4",1,219,"Southern Extension",27,4830,"Y","2017-06-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[372,"13-02-26-29-W4 &\n01-10-26-29-W4 &\n04-11-26-29-W4",2,168,"Petrogas - Airdrie Transmission",16,4960,"Y","2017-09-01","2021-05-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[373,"SE-34-026-29-W4 TO\nSE-36-026-01-W5","2,1",168,"Petrogas - Airdrie Transmission",37,4960,"Y","2017-09-01","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[374,"08-02-051-19-W4",3,60,"Viking-Edmonton Transmission - Line #3",24,4030,"Y","2018-01-01","2018-10-01","Defects Found","N","N/A","2020-03-01","No Repairs Required","N/A"]
[375,"13-13-51-25-W4",3,610,"Homeglen Transmission",10,6200,"Y","N/A","2017-09-01","Defects Found","Y",4535,"Not Required","Repairs Required","Y"]
[377,"8-30-52-21-W4",1,60,"Legal-Uncas Transmission",12,4960,"Y","2018-01-01","2020-01-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[378,"06-16-025-03-W5",2,114,"Jumping Pound West Transmission",8,5090,"Y","2017-08-01","2019-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[379,"11-20-42-25-W4",1,88,"Southern Extension",43,4830,"Y","2018-02-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[380,"LSD 10-19-82-25-W5",1,114,"Worsley-McLennan Transmission",52,4140,"Y","2018-06-01","2021-04-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[381,"9-5-57-8-W5 to 1-17-57-8-W5",1,219,"Mayerthorpe Branch",65,5520,"Y","2017-11-01","2021-02-21","Defects Found","N","N/A","2018-05-01","Repairs Required","N"]
[382,"16-12-54-25-W4",1,114,"St Albert-North Edmonton Lateral",7,3450,"Y","2017-11-01","2020-09-20","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[383,"SW-22-43-25-W4",1,168,"Southern Extension",49,4830,"Y","2018-03-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[384,"3-35-5-17-W4",1,33,"Taber-Coutts Branch (114.3)",8,6890,"Y","2017-12-01","2020-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[385,"LSD-12-10-45-7-W4M",1,33,"Fabyan Transmission",11,2070,"Y","2017-11-01","2018-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[386,"LSD 3-16-45-7-W4",1,114,"Fabyan Transmission",12,2070,"Y","2017-12-01","2018-10-01","Defects Found","Y","N/A","2018-11-01","Repairs Required","Y"]
[387,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",44,4830,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[388,"LSD 4-17-56-21-W4",1,219,"Redwater Transmission",6,4960,"Y","2018-02-01","2020-08-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[389,"SW-36-048-13-W4",1,168,"Birch Lake Transmission",8,4960,"Y","2017-06-01","2017-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[390,"2-33-65-10-W5M",1,60,"Swan Hills Transmission",11,6550,"Y","2018-06-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[391,"4-1-11-26-W4",1,114,"Granum Lateral",10,2070,"Y","2017-08-01","2018-05-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[392,"15-29-50-24-W4 to 2-4-51-24-W4","2,1",323,"Usona Transmission",44,7660,"Y","2017-10-01","2019-01-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[393,"SW-08-022-26-W4",2,60,"Carseland Transmission",8,6240,"Y","2017-06-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[394,"LSD 7-3-21-4-W5",1,48,"Millarville Transmission Line",15,3100,"Y","2017-11-01","2020-11-01","Defects Found","Y",2758,"Not Required","Repairs Required","Y"]
[395,"13-15-57-03-W5",1,60,"Swan Hills Transmission",10,6550,"Y","2017-10-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[396,"LSD 1-29-52-23-W4",2,60,"Viking-Edmonton Transmission - Line #3",75,2280,"Y","2018-01-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[397,"15-24-55-22-W4",2,114,"Bittern Lake to Redwater transmission",121,4960,"Y","2018-02-01","2019-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[398,"Sec 23-3-25-W4",1,114,"Cardston Transmission",30,3070,"Y","2017-08-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[399,"9-1-47-21-W4",1,60,"Southern Extension",26,4830,"N","N/A"]
[400,"16-19-38-1-W5M",1,88,"IS2228",18,6400,"Y","2017-09-01","2020-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[401,"SE-01-054-24-W4",3,60,"North Edmonton Loop",12,3450,"Y","2017-10-01","2019-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[402,"9-11-34-1-W5M",1,168,"Nevis - Airdrie",4,4960,"Y","2017-12-01","2019-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[403,"12-22-020-29-W4",3,114,"Mainline South (North)",13,4960,"Y","2017-11-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[404,"10-19-082-25-W5",1,114,"Worsley-McLennan Transmission",31,4140,"Y","2018-06-01","2020-01-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[405,"14-23-054-22-W4",1,26,"Legal-Uncas Transmission",5,3450,"Y","2017-12-01","2020-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[406,"NE-1-63-3-W4 to SE-6-63-2-W4",1,88,"Cold Lake Medley Transmission",36,3100,"Y","2017-11-01","2020-04-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[407,"NE-21-038-23-W4",1,88,"Cimarron Transmission",54,4960,"Y","2018-01-01","2018-09-01","Defects Found","N","N/A","2018-05-01","Repairs Required","Y"]
[408,"LSD-7-13-23-5-W5M",1,88,"Bragg Creek South Town Line",26,5830,"Y","2017-09-01","2020-09-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[409,"NW-34-049-23-W4",1,219,"Bittern Lake to Redwater transmission",7,9650,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[410,"07-15-089-09-W4",1,88,"Fort McMurray Transmission",18,6205,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[411,"NW-16-088-09-W4",1,114,"Fort McMurray Transmission",28,6205,"Y","2019-02-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[412,"SW-05-011-25-W4",1,168,"Fort Macleod Branch",80,4960,"Y","2017-09-01","2018-05-01","Defects Found","N","N/A","2019-02-01","No Repairs Required","N/A"]
[413,"SW-31-089-09-W4",1,114,"EXT198",24,6205,"Y","2016-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[414,"07-36-051-23-W4",1,168,"Bretona Transmission",70,4960,"Y","2017-11-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[415,"SE-10-052-24-W5",1,273,"Wabamun to Hinton Transmission",73,7240,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[416,"LSD 4-6-53-18-W4",1,60,"Mundare-Bruderheim Transmission",5,3450,"Y","2018-02-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[417,"1-28-50-9-W4",1,323,"Birch Lake Transmission",23,8450,"Y","2018-10-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[418,"15-31-050-25-W5",1,114,"Jasper Transmission",38,4960,"Y","2018-05-01",null,"Defects Found","N","N/A","2020-10-01","Repairs Required","N"]
[419,"SW-34-09-21-W4",1,273,"Lethbridge East #1 Branch (273.1)",47,2070,"Y","2017-09-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[420,"NE-36-048-13-W4",1,323,"Birch Lake Transmission",6,8450,"Y","2017-11-01","N/A","Defects Found","N","N/A","2019-04-01","Repairs Required","N"]
[421,"SW-31-71-10-W6",1,114,"Hythe-Beaverlodge Transmission",7,4140,"Y","2018-06-01","2020-06-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[422,"07-34-055-21-W4",1,406,"Shell Scotford Transmission",87,8450,"Y","2018-01-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[423,"01-30-055-22-W4",1,323,"Legal-Uncas Transmission",73,3447,"Y","2017-11-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[424,"SE-35-055-21-W4",1,323,"Esso Chemical Lateral",54,8450,"Y","2018-05-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[425,"04-17-050-02-W4",1,114,"Lloydminster Transmission",39,5520,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[426,"SW-21-056-23-W4",1,323,"Legal-Uncas Transmission",72,3447,"Y","2017-11-01",null,"Defects Found","N","N/A","2020-07-20","No Repairs Required","N/A"]
[427,"LSD 14-31-53-25-W4M",2,323,"Paddle River Transmission",169,5520,"Y","2017-06-01","2018-11-01","Defects Found","N","N/A","2020-01-01","Repairs Required","N"]
[428,"05-36-54-02-W5","3,2,1",219,"Paddle River Transmission",34,5520,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[429,"16-02-057-03-W5",1,323,"Swan Hills Transmission",13,6550,"Y","2017-12-01","2018-09-01","Defects Found","N","N/A","2018-10-01","No Repairs Required","N/A"]
[431,"09-03-051-11-W4",1,60,"Lavoy-Minburn Transmission",56,3450,"Y","2017-08-01","2018-06-01","Defects Found","N","N/A","2018-10-01","No Repairs Required","N/A"]
[432,"12-10-055-01-W5",1,323,"Swan Hills Transmission",44,6380,"Y","2018-02-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[433,"SE-36-050-26-W4",1,323,"Bonnie Glen Transmission",68,5520,"Y","2017-10-01","2019-09-01","Defects Found","N","N/A","2019-11-01","No Repairs Required","N/A"]
[434,"10-25-048-07-W5",1,114,"Pembina Transmission",180,6580,"Y","2018-02-01","2018-08-01","Defects Found","N","N/A","Not Started","Repairs Required","Y"]
[435,"05-01-074-11-W6",1,114,"Hythe-Beaverlodge Transmission",104,4140,"Y","2018-06-01","2020-08-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[436,"02-01-038-25-W4",1,88,"Nevis-Penhold",36,4960,"Y","2018-01-01","2018-09-01","Defects Found","N","N/A","2018-08-01","No Repairs Required","N/A"]
[437,"04-26-38-27-W4M",2,219,"Southern Extension \nPhase  1",12,4830,"Y","2018-02-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[438,"NE-17-006-20-W4",1,114,"Stirling Transmission",18,3070,"Y","2017-09-01","2021-04-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[439,"06-33-08-22-W4",1,88,"Willowbrook Lateral",58,4960,"Y","2017-08-01","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[440,"04-06-012-19-W4",1,60,"Turin East Transmission",7,6720,"Y","2017-08-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[441,"03-27-025-26-W4",1,60,"Strathmore Branch",15,6620,"Y","2017-11-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[442,"NW-33-40-26-W4M",2,219,"Southern Extension \nPhase  1",29,4830,"Y","2018-01-01","2020-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[443,"SW-25-025-07-W5",1,323,"Banff Loop (323.9)",46,4960,"Y","2017-10-01","2018-06-01","Defects Found","N","N/A","2020-07-20","No Repairs Required","N/A"]
[444,"03-10-39-27-W4M",2,219,"Southern Extension \nPhase  1",31,4830,"Y","2018-01-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[445,"NW-02-025-08-W5",1,323,"Banff Loop (323.9)",16,4960,"Y","2017-10-01","2018-08-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[446,"NW-12-40-26-W4M",2,219,"Southern Extension \nPhase  1",28,4830,"Y","2018-01-01","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[447,"SE-01-40-27-W4M",2,219,"Southern Extension \nPhase  1",45,4830,"Y","2018-01-01","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[448,"SE-15-39-27-W4M",2,219,"Southern Extension \nPhase  1",40,4830,"Y","2018-01-01","2021-08-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[449,"SE-23-025-05-W5",1,273,"273.1 Banff Loop",24,4960,"Y","2017-10-01","2018-07-01","Defects Found","N","N/A","2018-06-01","No Repairs Required","N/A"]
[450,"16-26-09-12-W4",1,60,"Yellow Lake Branch",14,3360,"Y","2017-09-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[451,"SW-01-40-27-W4M",2,219,"Southern Extension \nPhase  1",24,4830,"Y","2017-12-01","2020-06-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[452,"NEW-12-40-27-W4M",2,219,"Southern Extension \nPhase  1",95,4830,"Y","2018-02-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[453,"NW-23-39-27-W4M",2,219,"Southern Extension \nPhase  1",92,4830,"Y","2018-01-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[454,"NE-36-037-04-W4",1,88,"Provost",95,4140,"Y","2017-11-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[455,"15-15-047-07-W5",1,168,"Pembina Transmission",51,6580,"Y","2017-09-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[456,"01-04-55-20-W4M",2,508,"Inland-Ft Saskatchewan\nPhase  1",16,8450,"Y","2017-08-01","2020-08-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[457,"02-26-049-08-W4",1,168,"Vermilion Transmission",49,5170,"Y","2017-11-01","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[458,"02-33-050-06-W4",1,88,"Myrnam Transmission",13,8270,"Y","2017-12-01","2018-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[459,"NE-16-049-08-W5",1,114,"Pembina Transmission",81,9930,"Y","2017-11-01","2018-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[460,"16-35-24-29-W4",3,406,"Temple Gate Lateral",5,5090,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[461,"NW-31-050-07-W5",1,26,"IS5161",1,8274,"Y","2017-11-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[462,"NW-13-49-27-W5 &\nNW-19-49-26-W5 &\nSE-30-49-26-W5 &\nNW-29-49-26-W5",1,114,"Jasper Transmission",22,6900,"Y","2017-11-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[463,"SE 07-08-05-W5 TO\nSW 16-08-05-W5",1,60,"Summit Lime Transmission",45,5820,"Y","2017-08-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[464,"14-10-039-27-W4",1,168,"Southern Extension",16,4830,"Y","2018-03-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[465,"13-33-40-26-W4M",1,168,"Southern Extension",8,4830,"Y","2018-03-01","2021-04-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[467,"11-025-08-W5",1,219,"Banff Transmission",35,4960,"Y","2017-09-01","2018-08-01","Defects Found","N","N/A","2020-01-01","No Repairs Required","N/A"]
[468,"NE-25-51-23-W4",1,168,"Bretona Transmission",63,4960,"Y","2017-11-01",null,"Defects Found","N ","N/A","Not Started","Unknown","N"]
[469,"12-29-40-15-W4",1,26,"Forestburg Generating Plant Transmission",136,8450,"Y","2018-02-01","N/A","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[470,"NW-21-06-21-W4",1,114,"Cardston Transmission",27,3070,"Y","2017-09-01","2021-04-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[471,"SE-24-050-26-W4",1,406,"Pembina Loop",114,6140,"Y","2017-09-01","2018-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[472,"14-17-006-20-W4",1,114,"Stirling Transmission",63,3070,"Y","2017-08-01","2021-04-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[473,"15-10-095-06-W4",1,88,"Firebag Lateral",15,9930,"Y","2019-02-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[474,"SW-23-049-26-W4",1,323,"Bonnie Glen Transmission",31,5520,"Y","2017-11-01","2019-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[475,"02-09-043-25-W4",3,60,"Southern Extension",23,4830,"Y","2017-12-01","2021-03-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[476,"SE-13-42-26-W4 to SW-26-42-25-W4M",1,60,"Southern Extension",10,4830,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[477,"LSD 14-12-23-5-W5 to LSD 4-13-23-5-W5",2,88,"Bragg Creek South Town Line",22,5830,"Y","2017-10-01","2020-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[478,"NW-22-041-26-W4 TO NE-35-041-26-W4",1,60,"Southern Extension",10,4830,"Y","2018-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[479,"3-22-43-25-W4M",1,60,"Southern Extension",14,4830,"Y","2018-11-01","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[480,"14-04-43-25-W4M",2,168,"North Ponoka Lateral",27,4830,"Y","2018-01-01","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[481,"NE-9-41-26-W4M","2,1",114,"Southern Extension",54,4830,"Y","2018-01-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[482,"10-28-45-28-W4 & 4-2-46-28 W4",1,610,"Homeglen Transmission",12,6200,"Y","N/A","2017-08-01","Defects Found","N","N/A","2017-08-01","Repairs Required","Y"]
[483,"NE-3-45-24-W4 to NE 20-46-22-W4",1,60,"Southern Extension",67,4830,"Y","2018-02-01","2020-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[484,"NE-30-042-09-W4 to NW-30-042-09-W4",1,60,"Irma - Hardisty Transmission",27,6205,"Y","2017-11-01","2018-04-01","Defects Found","N","N/A","2019-02-01","No Repairs Required","N/A"]
[485,"SE-13-052-23-W4",1,60,"Bretona Transmission",8,4960,"Y","2017-11-01","2019-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[486,"NE-19-40-26-W4M",2,219,"Southern Extension \nPhase  1",24,4830,"Y","N/A","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[487,"SE-32-40-26-W4M",2,219,"Southern Extension \nPhase  1",20,4830,"N","N/A"]
[488,"NW-18-037-27-W4",2,168,"Nevis - Airdrie",10,4960,"N","N/A"]
[489,"08-05-049-07-W5",1,88,"Pembina Lobstick Transmission",12,3720,"Y","2018-03-01","2018-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[490,"15-24-9-26-W4M",1,168,"Fort MacLeod Branch",28,2070,"Y","2017-09-01","2018-05-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[491,"16-36-35-1-W5M","2,1",48,"Anthony Henday Branch",19,4960,"Y","2018-02-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[492,"03-20-21-29-W4",1,323,"Banff Loop (323.9)",12,4960,"Y","N/A","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[493,"NE-34-47-19-W4",1,219,"Southern Extension",23,4830,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[494,"NE-10-47-20-W4",1,219,"Southern Extension",75,4830,"Y","2017-11-01",null,"Defects Found","Y","N/A","Not Started","Repairs Required","Y"]
[495,"NW-07-49-17-W4",1,219,"Southern Extension",20,4830,"Y","2017-11-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[496,"SE-33-37-27-W4",2,168,"Nevis - Airdrie",4,4960,"N","N/A"]
[497,"LSD 4-24-24-3-W5",2,323,"Jumping Pound Transmission",4,4960,"Y","N/A","2021-01-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[498,"LSD 8-2-20-28-W4 & 5-3-20-27-W4",1,219,"Arrowwood Transmission",7,6620,"Y","N/A","2019-02-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[499,"LSD 3-6-20-28-W4",1,219,"Arrowwood Transmission",5,6620,"Y","N/A","2019-02-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[500,"2-29-22-3-W5M",1,406,"Priddis Transmission Line (406.3)",27,6140,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[501,"S-27-038-27-W4",2,168,"Nevis Transmission",12,4960,"N","N/A"]
[502,"09-09-16-24-W4M",3,88,"Vulcan Transmission",8,6620,"Y","2017-08-01","2020-10-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[503,"04-034-047-09-W5",1,114,"Pembina Transmission (#7 Receipt Station)",65,6690,"Y","2017-11-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[504,"SW-29-6-25-W4M to NW-16-6-25-W4M",1,60,"Standoff Transmission",72,6720,"Y","2017-09-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[505,"07-08-020-02-W5",3,114,"Turner Valley 3",18,2130,"Y","N/A","2018-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[506,"12-12-35-01-W5",1,60,"Innisfail West Branch",1,4960,"Y","2017-12-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[507,"16-05-30-01-W5","3,1",114,"Nevis-Airdrie",14,4960,"Y","2017-11-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[508,"7-8-29-22-W4M","2,1",406,"Carbon Transmission",40,5520,"Y","2017-11-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[509,"LSD 4-14-10-12-W4",2,168,"Foremost Transmission",6,4970,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[510,"LSD 2-14-10-16-W4",1,88,"Mainline East",6,4960,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[511,"LSD 5-5-10-19-W4M","2,1",323,"Mainline East",6,4960,"Y","2017-11-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[512,"LSD 5-13-25-5-W5M","2,1",323,"Jumping Pound Transmission",34,4960,"Y","2017-10-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[513,"NW-22-020-29-W4",2,323,"Mainline South (North)",4,4960,"Y","N/A","2021-05-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[514,"13-8-11-10-W4","2,1",60,"Bow Island Delivery Branch",21,3380,"Y","2019-01-01","N/A","Defects Found","N","N/A","2020-04-01","No Repairs Required","N/A"]
[515,"14-33-24-28-W4 to 3-4-25-28-W4",2,406,"Carbon Transmission",8,5520,"Y","N/A","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[517,"SW-22-045-25-W4",1,168,"Southern Extension",42,4830,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[518,"LSD 16-34-24-4-W5M",1,323,"Jumping Pound Transmission",51,4960,"Y","2017-10-01","2019-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[519,"06-33-20-29-W4M",3,114,"Mainline South (North)",17,4960,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[520,"LSD 15-12-24-26-W4",1,406,"Carseland Transmission",6,6240,"Y","2017-11-01","2019-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[521,"8-28-20-29-W4M","3,2",323,"Mainline South",19,4960,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[522,"NW-01-044-04-W4",1,60,"Edgerton Town Line",14,8260,"Y","2017-11-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[523,"3-21-53-23-W4M",2,323,"Cloverbar Compressor Bypass",36,8450,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[524,"02-14-25-28-W4",1,508,"Carbon Transmission",32,5520,"Y","2017-11-01","2018-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[525,"5-15-25-2-W5",3,406,"Jumping Pound West Transmission",18,5090,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[526,"07-22-39-22-W4M",2,88,"Alix, Mirror, Bashaw Transmission",23,4960,"Y","2017-12-01","N/A","Defects Found","N","N/A","2019-10-01","No Repairs Required","N/A"]
[527,"14-30-42-09-W4M to 10-30-42-09-W4M",1,114,"Irma-Hardisty Transmission",106,6205,"Y","2017-11-01",null,"Defects Found","N","N/A","2018-11-01","No Repairs Required","N/A"]
[528,"11-36-23-02-W5M",2,323,"Jumping Pound Transmission",4,4960,"Y","2017-11-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[529,"NW 9-51-26-W4M",1,114,"Pine Valley Transmission",49,6895,"Y","2017-11-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[530,"5-7-20-2-W5M",2,168,"Turner Valley",9,2080,"Y","2017-12-01","2018-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[531,"NW-12-38-27-W4M to NW-11-38-27-W4M","3,2",88,"Nevis-Airdrie",20,4960,"Y","2017-11-01","2018-10-01","Defects Found","N","N/A","2018-10-01","No Repairs Required","N/A"]
[532,"6-33-24-10-W5M",3,168,"Banff Transmission",8,4960,"Y","2017-11-01","N/A","Defects Found","N","N/A","2020-01-01","No Repairs Required","N/A"]
[535,"4-26-46-24-W4",2,60,"Southern Extension",4,4830,"Y","2017-11-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[536," 15-23-56-25-W4M",1,168,"Manawan Lake Lateral ",106,6580,"Y","2017-12-01","2020-08-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[537,"16-27-54-2-W5M",3,273,"Onoway-Wabamun Transmission",6,4830,"Y","2018-03-01","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[538,"2-10-49-6-W5",1,114,"Berrymoore Lateral 1 &2",63,6140,"Y","2017-11-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[539,"2-29-57-21-W4M",2,168,"Redwater Transmission",80,4960,"Y","2017-12-01","2020-08-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[540,"16-7-72-5-W6M to 13-8-72-5-W6M",2,114,"Hermit Lake Transmission",21,6550,"Y","2018-06-01","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[541,"07-17-56-21-W4M","2,1",168,"Bittern Lake Transmission",22,4830,"Y","2017-12-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[542," 4-11-53-4-W5M",2,273,"Wabamun - Onoway Transmission",9,4830,"Y","2018-03-01","N/A","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[543,"3-16-51-19-W4M","2,1",406,"Viking Transmission",22,4030,"Y","2017-11-01","N/A","Defects Found","N","N/A","2018-08-01","No Repairs Required","N/A"]
[544,"SE-29-50-4-W4M to NE-20-50-4-W4M",1,60,"Islay Branch",53,5520,"Y","2017-12-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[545,"08-17-050-07-W5",1,168,"Pembina Lobstick Transmission",23,8274,"Y","2018-01-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[546,"01-02-20-28-W4",1,406,"Mazeppa-Canoxy Tranmission",2,6620,"N",null,"N/A"]
[547,"03-01-095-11-W4",1,60,"TransCanada Fort Mackay",13,9930,"Y","2019-02-01","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[548,"SW-9-78-21-W5M",2,114,"Worsley-McLennan Transmission",73,4140,"Y","2018-08-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[549,"10-08-47-27-W4",1,114,"Homeglen Transmission",40,6200,"Y","2017-11-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[550,"SE-25-56-6-W5M",2,88,"Paddle River Transmission",9,5520,"Y","2018-01-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[551,"05-24-53-05-W5",1,273,"Hinton-Wabamun Transmission",25,7240,"Y","2017-11-01","2018-10-01","Defects Found","N","N/A","Not Started","Repairs Required","Y"]
[552,"5-23-49-26-W4M",1,114,"Homeglen Transmission",6,6200,"Y","2017-09-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[553,"09-12-52-23-W4M",2,168,"Bretona Transmission",4,4960,"Y","2017-11-01","N/A","Defects Found","Y","N/A","Not Required","Repairs Required","Y"]
[554,"LSD 12-7-82-21-W5",1,114,"Worsley-McLennan Transmission",2,4140,"Y","N/A","2020-02-01","Defects Found","Y","N/A","Not Required","Repairs Required","Y"]
[555,"10-9-53-23-W4M",2,219,"East Edmonton Interconnection",14,4960,"Y","2018-08-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[556,"4-29-71-09-W6M, 5-29-71-9-W6M, 4-6-72-9-W6M",1,60,"Hythe-Beaverlodge Transmission",8,4140,"Y","2018-03-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[557,"1-3-53-27-W4M",3,114,"Stony Plain Transmission",12,3450,"Y","2018-05-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[558,"2-5-55-22-W4M",1,88,"Fort Sask North Edmonton Lateral",10,3450,"Y","2018-05-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[559,"2-13-53-28-W4M",1,168,"Parkland to Stony Plain Transmission",69,6380,"Y","2017-11-01","N/A","Defects Found","N","N/A","2018-02-01","No Repairs Required","N/A"]
[560," SW 8-49-7-W5M",2,88,"Pembina Lobstick Transmission",16,3720,"Y","2017-12-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[561,"15-13-73-11-W6M",1,114,"Hythe-Beaverlodge Transmission",9,4140,"Y","2018-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[562,"12-36-71-7-W6M",2,219," Hermit Lake",17,6550,"Y","2018-06-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[563,"SE-13-50-03-W4M","2,1",168,"Lloydminster Transmission",14,5520,"Y","2017-11-01","2019-01-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[564,"SW-35-023-29-W4 TO SE-36-023-29-W4",2,219,"Chestermere Lake Loop",33,5090,"Y","2017-11-01","2020-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[565,"16-13-54-3-W5M",1,273,"Wabamun - Onoway Transmission",2,4830,"Y","2018-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[566,"12-52-23-W4M to 13-52-23-W4M",2,168,"Bretona Transmission",57,4960,"Y","2017-12-01","2019-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[567,"3-12-53-26-W4M",3,114,"Acheson Transmission",13,3450,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[568,"15-07-51-09-W5M",2,219,"Wildwood Lateral",1,9930,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[569,"NW 23-51-27-W4M",2,114,"Pine Valley Transmission",73,6895,"Y","2017-12-01","2018-03-01","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[570,"08-17-045-07-W4",1,33,"Fabyan Transmission",4,1900,"Y","N/A","2018-10-01","Defects Found","N","N/A","2019-11-01","No Repairs Required","N/A"]
[571,"4-28-51-24-W4M",1,219,"Golden Spike Transmission",28,6200,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[572,"01-01-57-03-W5M",1,323,"Swan Hills Transmission",14,6380,"Y","2018-01-01","2018-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[573,"14-19-52-23-W4M","3,2",406,"Viking 3 and 4",9,4030,"Y","2018-10-01","2019-01-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[574,"NE-3-56-22-W4M to NE-12-56-22-W4M",1,323,"Redwater Transmission",64,4960,"Y","2017-12-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[576,"NW-24-53-28-W4M",1,114,"Swan Hills Transmission",12,6380,"Y","2017-11-01","2019-01-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[577,"4-31-52-27-W4M",2,114,"Stony Plain Gate 2 Lateral",18,3450,"Y","2018-03-01","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[578,"01-27-51-27-W4M",2,168,"Buckwheat",1,6070,"Y","2018-02-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[579,"SE-26-054-01-W5",1,114,"Paddle River Transmission",11,5520,"Y","2017-10-01","2018-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[580,"04-06-39-26-W4M",2,219,"Southern Extension",11,4830,"Y","2017-12-01","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[581,"NW-10-54-24-W4M","3,2",114,"North Edmonton Branch Line ",57,3450,"Y","2018-02-01","2019-05-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[582,"13-36-055-23-W4",1,42,"Legal-Uncas Transmission",6,3447,"Y","2018-03-01","2020-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[583,"05-27-56-06-W5M",1,273,"Paddle River Transmission",2,5520,"Y","N/A","2018-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[584,"1-1-11-11-W4M",3,114,"Bow Island Branch",9,3380,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[585,"15-10-056-22-W4",1,323,"Redwater Transmission",39,4960,"Y","2017-11-01","2021-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[586,"13-12-74-04-W6M",1,88,"Teepee Creek Transmission",8,4960,"Y","2018-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[587,"SW 06-48-26-W4 &\nSW 17-48-26-W4",1,323,"Bonnie Glen Transmission",20,6205,"Y","2018-03-01",null,"Defects Found","N","N/A","Not Started","Unknown","N"]
[588,"NW 10-55-1-W5M",1,323,"Swan Hills Transmission",8,6380,"Y","2017-11-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[589,"03-18-019-13-W4 &\n12-07-019-13-W4",1,114,"Princess - Brooks Transmission",14,2070,"Y","2017-12-01","2019-11-01","Defects Found","N","N/A","2020-03-01","No Repairs Required","N/A"]
[590,"SE-06-70-05-W6",2,33,"Gold Creek Transmission",6,6550,"Y","2018-03-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[592,"NW/SW-27-53-25-W4M","3,2",323,"North Edmonton Loop",42,3450,"Y","2018-03-01","2019-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[593,"SW 4-52-24-W4M",3,508,"Southeast Edmonton Transmission",19,5520,"Y","2017-11-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[594,"05-13-61-07-W5M",1,114,"Swan Hills Transmission",27,6550,"Y","2018-02-01","2018-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[601,"SE 29-52-23-W4 to NE-20-52-23-W4",2,60,"Viking-Edmonton - Loops & Branches",16,2280,"Y","N/A","2021-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[603,"8-27-27-25-W4",1,406,"Carbon Transmission",6,5520,"Y","N/A","2016-08-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[604,"SE-23-063-02-W4",3,60,"NOVA-Grande Centre-Cold Lake Transmission",2,4140,"N","N/A"]
[606,"3-10-39-27-W4M to 12-4-41-26-W4M",2,168,"Southern Extension",1,4830,"N","N/A"]
[607,"15-25-071-06-W6",3,168,"Grande Prairie Transmission",3,6550,"N","N/A"]
[621,"LSD 13-2-21-4-W5",1,48,"Millarville Transmission Line",11,3100,"Y","N/A","2021-06-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[622,"LSD-11-25-52-26-W4M",2,88,"Swan Hills Transmission",4,6200,"Y","N/A","2018-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[626,"LSD 7-15-51-21-W4",1,60,"Golden Tie-in Loop",6,4270,"Y","N/A","2018-08-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[629,"1-20-51-24-W4 to 1-17-51-24-W4",2,323,"Usona Transmission",21,7660,"Y","N/A","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[631,"NW-26-83-22-W5",2,114,"Worsley-McLennan Transmission",12,4140,"Y","N/A","2019-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[634,"SE-35-49-26-W4",1,323,"Bonnie Glen Transmission",3,6205,"Y","N/A","2019-08-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[642,"NE-36-54-3-W5",1,42,"Wabamun - Onoway Transmission",4,4830,"N","N/A"]
[644,"04-31-53-23-W4M",3,406,"Namao Transmission ",2,3450,"N","N/A"]
[647,"02-04-53-26-W4M",2,168,"Stony Plain Transmission",2,3450,"Y","N/A","2018-09-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[648,"04-33-71-6-W6M",2,219,"Hermit Lake",8,6550,"Y","2020-05-01","2020-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[649,"NW-06-082-21-W5",1,114,"Worsley-McLennan Transmission",12,4140,"N","N/A"]
[652,"04-31-53-23-W4M",3,323,"North Edmonton Loop",2,3450,"N","N/A"]
[654,"08-25-78-26-W5M",3,42,"Eaglesham Superbox FTU",8,6720,"Y","N/A","2019-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[655,"NW-27-053-25-W4",3,219,"Paddle River Transmission",8,5520,"Y","N/A","2018-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[661,"LSD 15-29-53-25-W4",3,323,"Paddle River Loop",6,8480,"Y","N/A","2018-06-01","Defects Found","N","N/A","2018-09-01","No Repairs Required","N/A"]
[663,"SE-06-53-25-W4M",2,168," Acheson Transmission",2,3450,"Y","N/A","2019-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[664,"16-02-48-04-W5M","3,2",60,"Pembina Transmission",1,6140,"Y","N/A","2018-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[665,"8-25-9-12-W4M",1,60,"Yellow Lake Lateral",10,3360,"Y","N/A","2018-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[666,"14-32-10-12-W4M","2,1",273,"Mainline East (East) ",1,4960,"Y","N/A","2020-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[671,"13-14-49-01-W5M",2,88,"Pembina Transmission",2,6140,"Y","N/A","2018-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[672," 8-25-46-22-W4M",1,168,"Bittern Lake Transmission",2,8140,"Y","N/A","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[673," 10-18-56-23-W4M",3,33,"Bon Accord Town Lateral",1,3450,"Y","N/A","2020-05-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[675," 11-29-50-3-W4M",2,88,"Lloydminster Transmission",2,5520,"Y","N/A","2019-01-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[676," 5-55-22-W4M","2,1",88,"Legal-Uncas Transmission",15,3447,"Y","N/A","2019-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[678," 16-4-49-8-W5M",1,168,"Pembina Transmission",2,6140,"Y","N/A","2018-08-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[679," 7-25-50-25-W4M",2,114,"Nisku Industrial Lateral",14,6140,"N","N/A"]
[682,"1-27-48-3-W5M",1,168,"Pembina Transmission",2,6140,"Y","N/A","2018-08-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[685,"15-8-54-24-W4M to 13-9-54-24-W4M",2,114,"North Edmonton Loop",18,3450,"Y","N/A","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[692,"SW-30-24-28-W4M",3,508,"Shepard",84,6240,"Y","2016-01-01","2016-01-01","Defects Found","N","N/A","2016-06-01","Repairs Required","Y"]
[693,"SE-36-23-29-W4M & SW-35-23-29-W4M",2,508,"Shepard",133,6240,"Y","2015-12-01","2015-12-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[694,"08-25-23-29- W4M",2,508,"Shepard",131,6240,"Y","2015-12-01","2015-12-01","Defects Found","Y",4635,"2016-06-01","Repairs Required","Y"]
[695,"SW-20-23-26-W4M",2,508,"Shepard",36,6240,"Y","2015-12-01","2015-12-01","Defects Found","N","N/A","Not Required","Repairs Required","Y"]
[703,"NE-25-052-24-W4",2,60,"East Edmonton Interconnection",2,3450,"Y","N/A","2021-05-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[708,"NW-11-062-08-W5 & NW-22-061-07-W5",1,26,"Swan Hills Transmission",2,6550,"Y","N/A","2019-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[709,"SE-16-83-23-W5",1,60,"Worsley-McLennan Transmission",2,4140,"Y","N/A","2019-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[714,"1-13-52-23-W4M and 8-13-52-23-W4M",2,168,"Bretona Transmission",4,4960,"Y","N/A","2019-10-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[716,"9-35-48-3-W5",2,33,"Pembina Transmission",3,6550,"Y","N/A","2018-08-01","Defects Found","N","N/A","2018-09-01","No Repairs Required","N/A"]
[719,"NE-07-083-23-W5",3,114,"Worsley-McLennan Transmission",12,4140,"N","N/A"]
[720,"SW-27-035-28-W4",2,168,"Nevis - Airdrie",2,4960,"Y","N/A","2019-04-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[722,"NE-18-09-21-W4",3,33,"Hardieville Lateral",2,2070,"Y","N/A","2018-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[723,"NE-23-028-01-W5",3,88,"Nevis - Airdrie",14,4960,"N","N/A"]
[724,"NE-25-071-06-W6",3,168,"EXT58",10,6550,"N","N/A"]
[725,"14-21-042-02-W5 TO\n15-21-042-02-W5",2,60,"Rimbey Nova South Transmission",10,6200,"Y","N/A","2020-07-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[726,"7-32-39-22-W4",1,88,"Alix, Mirror, Bashaw Transmission",10,4960,"Y","N/A","2021-04-21","Defects Found","N","N/A","Not started","Unknown","N"]
[731,"SW-02-053-26-W4",1,168,"Swan Hills Transmission",95,3450,"N","N/A"]
[732,"19-053-26-W4 TO \n20-053-26-W4",1,60,"Swan Hills Transmission",42,6380,"N","N/A"]
[733,"16-05-49-07-W5M","3,2",88,"Pembina Lobstick Transmission",50,3720,"Y","N/A","2018-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[735,"16-27-22-29-W4",3,406,"Priddis Transmission Line (406.3)",48,6140,"Y","2018-06-01","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[736,"LSD 14-8-47-27-W4",1,60,"Mulhurst Lateral",10,6210,"Y","N/A","2019-09-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[742,"10-15-29-23-W4M",2,60,"Carbon Town Branch",12,5515,"Y","N/A","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[743,"LSD 8/9/16/17-53-23-W4",2,114,"East Edmonton Interconnection",26,4960,"Y","N/A","2019-09-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[746,"NE-2-50-1-W4",2,88,"Lloydminster Transmission",11,5520,"Y","N/A","2019-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[747,"LSD 9-24-81-21-W5",2,60,"Nampa Branch Line ",8,4140,"N","N/A"]
[749,"LSD 1-20-52-23-W4",2,60,"Viking-Edmonton - Loops & Branches",8,2275,"Y","N/A","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[753,"NW-12-053-04-W5 &\nSW-13-053-04-W5","2,1",273,"Wabamun - Onoway Transmission",14,4830,"N","N/A"]
[758,"SW-25-057-25-W4",3,114,"Legal-Uncas Transmission",10,3447,"Y","N/A","2019-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[760,"SW 14-55-04 W5",1,42,"Paddle River Transmission",8,5520,"Y","2017-11-01","2018-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[761,"NW 27-53-25-W4 &\nS-34-53-25-W4","3,1",219,"Villeneuve Transmission",18,8480,"Y","N/A","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[762,"NW-34-052-27-W4",2,60,"Stony Plain Transmission",6,3450,"Y","2018-03-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[764,"NE-31-055-21-W4",2,168,"Bittern Lake to Redwater transmission",20,4960,"N","N/A"]
[765,"NW-06-054-23-W4 &\nNW-01-54-24-W4",3,323,"Villeneuve Transmission",4,8480,"Y","N/A","2018-05-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[766,"09-01-054-25-W4",3,323,"Villeneuve Transmission",4,8480,"Y","N/A","2018-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[767,"05-08-54-24-W4 TO \n08-08-54-24-W4",3,406,"Namao Loop/North Edmonton Loop",7,3450,"Y","N/A","2021-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[768,"S-05-053-25-W4",2,219,"Acheson Transmission",26,3450,"Y","N/A","2019-08-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[769,"SW-11-054-24-W4",2,406,"Villeneuve Transmission",12,3450,"Y","N/A","2018-05-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[770,"8-4-55-22-W4 to 5-3-55-22-W4","2,1",273,"Bittern Lake to Redwater transmission",3,4140,"Y","N/A","2019-07-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[771,"LSD 8-10-28-24-W4",1,33,"Carbon Transmission",2,5520,"Y","N/A","2018-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[772,"8-19-52-23-W4",1,168,"Viking-Edmonton - Loops & Branches",4,2275,"N","N/A"]
[773,"NE-25-51-23-W4",1,88,"Bretona Transmission",14,4960,"N","N/A"]
[774,"NE-36-71-5-W6",1,88,"Hermit Lake",8,6550,"Y","N/A","2020-02-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[775,"LSD 7-17-47-27-W4 to LSD 2-17-47-27-W4",1,114,"Bonnie Glen Transmission",66,5520,"Y","N/A","2020-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[776,"LSD 8-24-50-26-W4",1,33,"Pembina Loop",2,6140,"Y","N/A","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[777,"E1/2-33-54-22-W4",1,114,"Legal-Uncas Transmission",16,4450,"Y","N/A","2019-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[778,"LSD 6-15-8-21-W4",1,33,"Cardston Transmission",1,3070,"Y","N/A","2020-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[779,"LSD 4-14-51-26-W4",1,168,"Pine Valley Transmission",13,6895,"N","N/A"]
[780,"NE-36-11-20-W4",1,60,"Turin East Transmission",12,6720,"N","N/A"]
[782,"NE-31-53-23-W4",1,60,"Kuhlmann Lateral",10,3450,"Y","N/A","2020-09-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[783,"LSD 4-2-49-13-W4 & NE-16-52-21-W4",1,406,"Viking-Edmonton Transmission - Line #3",6,4030,"Y","N/A","2018-08-01","Defects Found","N","N/A","2020-01-01","No Repairs Required","N/A"]
[784,"SE-20-053-23-W4",2,273,"Ardrossan Transmission",7,3100,"Y","N/A","2019-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[786,"LSD 15-8-14-18-W4",1,88,"Vauxhall Transmission",2,6620,"Y","N/A","2019-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[787,"LSD 1-1-20-29-W4",1,26,"Arrowwood Transmission",1,6620,"Y","N/A","2019-02-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[788,"SE-16-053-21-W4",1,33,"Bretona Receipt Lateral",6,4210,"Y","N/A","2020-01-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[789,"LSD-16-33-44-24-W4M",1,60,"Louis Bull Branch",8,4830,"N","N/A"]
[791,"NW-8-14-23-W4M",1,88,"Vulcan Transmission",8,6620,"N","N/A"]
[792,"SW 21-47-08-W4 &\nSE 15-47-08-W4 &\nSW 05-47-07-W4 &\nNW 25-46-07-W4",1,273,"Auburndale East Transmission",7,4960,"Y","N/A","2019-04-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[793,"NE-22-071-07-W6",1,114,"Bearhills Wembley Branch Line",4,6550,"Y","N/A","2020-02-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[794,"13-24-052-22-W4 &\n16-23-52-22-W4",1,406,"Viking-Edmonton Transmission - Line #4",2,4030,"Y","N/A","2019-04-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[795,"05-10-054-24-W4",1,406,"North Edmonton Loop",0,3450,"N","N/A","N/A","N/A","N/A","N/A","N/A","N/A","N - Piping Removed"]
[797,"SE-21-039-22-W4",1,88,"Alix, Mirror, Bashaw Transmission",12,4960,"N","N/A"]
[802,"NW-12-051-23-W4",1,168,"Bretona Transmission",3,4960,"Y","N/A","2019-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[805,"SE-26-051-25-W4",1,219,"Golden Spike Transmission",54,6200,"Y","N/A","2021-02-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[806,"14-21-07-17-W4 &\n15-21-07-17-W4",1,60,"Wrentham #2 Lateral (60.3)",16,1900,"N","N/A"]
[807,"NE-08-052-21-W4",1,42,"Viking-Edmonton - Loops & Branches",7,2210,"Y","N/A","2018-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[809,"15-35-053-25-W4",1,323,"Villeneuve Transmission",17,8480,"Y","N/A","2021-09-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[810,"04-06-055-22-W4",1,273,"Bittern Lake to Redwater transmission",10,4140,"Y","N/A","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[811,"04-05-057-21-W4",1,168,"Bittern Lake to Redwater transmission",2,4960,"Y","N/A","2019-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[812,"14-26-022-26-W4",1,60,"Carseland Branch",16,3100,"Y","N/A","2019-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[814,"NE-34-052-22-W4",1,60,"Viking-Edmonton - Loops & Branches",15,5085,"Y","N/A","2019-01-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[815,"04-02-010-19-W4",1,33,"Mainline East (West)",1,4960,"Y","N/A","2020-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[816,"16-32-069-06-W6",1,60,"Grovedale",8,8270,"Y","N/A","2020-06-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[817,"10-18-019-14-W4",1,60,"Brooks Lakeside Feeders Tr.Line",4,4970,"Y","N/A","2021-04-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[818,"03-18-028-23-W4 &\n14-17-028-23-W4",1,114,"PCP - Entice Transmission",12,5520,"N","N/A"]
[819,"SE 28-38-03 W4",1,88,"Provost",12,4140,"N","N/A"]
[820,"14-28-09-21-W4",1,42,"Mainline East",2,4960,"Y","N/A","2020-02-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[821,"08-34-011-20-W4",1,42,"Turin East Transmission",2,6720,"N","N/A"]
[822,"13-09-013-23-W4",1,42,"Vulcan Transmission",2,6620,"Y","N/A","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[824,"05-18-024-02-W5",1,33,"Jumping Pound Transmission",3,4960,"Y","N/A","2020-02-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[825,"12-04-055-22-W4",1,273,"Bittern Lake to Redwater transmission",2,4140,"N","N/A"]
[826,"16-02-054-24-W4",1,323,"North Edmonton Loop",10,3450,"Y","N/A","2019-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[828,"5-11-47-20-W4",1,114,"Southern Extension",12,4830,"N","N/A"]
[830,"12-35-09-19-W4M",1,33,"Coaldale East #2 Branch",2,2380,"Y","N/A","2020-04-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[831,"SW-17-9-21-W4M",3,42,"Lethbridge West Branch",3,2070,"Y","N/A","2018-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[832,"08-01-11-11-W4",3,42,"Bow Island Branch",2,3380,"Y","N/A","2020-08-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[833,"08-29-09-16-W4","2,1",42,"Taber Bend South Lateral",2,4960,"Y","N/A","2020-07-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[835,"13-32-09-22-W4",1,42,"Mainline East (West)",2,4960,"Y","N/A","2020-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[836,"14-16-06-11-W4M",2,88,"Foremost Branch Line",22,4970,"N","N/A"]
[837,"NE-22-39-27-W4M","3,2",60,"Blackfalds West Branch",22,4820,"N","N/A"]
[838,"9-29-37-27-W4M to 5-34-37-27-W4M","3,2",168,"Nevis-Airdrie",8,4960,"Y","N/A","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[839,"LSD 9-29-37-27-W4M ","3,2",168,"Nevis-Airdrie",6,4960,"Y","N/A","2019-05-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[841,"LSD 3-21-25-29-W4",2,323,"Jumping Pound Transmission",2,4960,"Y","N/A","2020-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[842,"LSD SE 35-24-4-W5M",1,323,"Jumping Pound Transmission",8,4960,"Y","N/A","2021-02-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[843,"04-02-10-12-W4",1,88,"Yellow Lake Branch",1,3360,"Y","N/A","2018-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[845,"SE-34-38-01-W5M",1,168,"Sylvan Lake Transmission",6,4690,"Y","N/A","2021-01-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[846,"SE-6-17-28-W4",1,60,"Willow Creek Branch",11,2070,"Y","N/A","2020-07-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[847,"NW-11-50-1-W4",2,88,"Lloydminster Branch",12,5520,"Y","N/A","2019-01-01","Defects Found","N","N/A","2020-03-01","No Repairs Required","N/A"]
[848,"1-23-25-1-W5",2,42,"Jumping Pound West Transmission",1,5090,"Y","N/A","2021-05-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[849,"15-21-24-3-W5",2,42,"Jumping Pound Transmission",2,4960,"Y","N/A","2020-09-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[850,"4-11-20-29-W4",1,323,"Mainline South",2,4960,"Y","N/A","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[851,"13-52-23-W4M to 24-52-23-W4M",2,168,"Bretona Transmission",110,4960,"N","N/A"]
[853,"10-16-56-23-W4M",1,323,"Legal-Uncas Transmission",2,3450,"Y","N/A","2019-12-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[854,"09-20-52-23-W4M",2,60,"Viking Transmission",2,2280,"Y","N/A","2018-10-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[856,"11-25-53-27-W4M, 01-17-53-26-W4M, 04-30-52-25-W4M",2,27,"Swan Hills Transmission",6,6380,"Y","N/A","2019-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[858,"01-05-53-26-W4M, 09-34-52-27-W4M, 16-36-52-27-W4M","3,2,1",27,"Stony Plain Transmission",3,3450,"Y","N/A","2018-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[859,"08-04-49-26-W4M & 16-33-48-26-W4M",1,27,"Bonnie Glen Transmission",4,5520,"Y","N/A","2019-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[860,"12-12-53-22-W4",1,273,"Ardrossan Transmission",2,3100,"Y","N/A","2019-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[864,"14-21-52-23-W4M",3,508,"East Edmonton Interconnection",2,4960,"Y","2018-10-01","N/A","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[866,"14-10-51-22 W4",2,114,"Bretona Transmission",13,4960,"N","N/A"]
[869,"13-20-88-08-W4M",2,114,"Fort McMurray Transmission",12,6200,"Y","N/A","2019-02-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[870,"SE-10-54-24-W4M",2,"219/323","North Edmonton Loop",115,3450,"Y","N/A","2021-07-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[872,"03-13-66-10-W5M",2,88,"Swan Hills Transmission",10,6550,"Y","N/A","2020-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[873,"NW-28-20-14-W4M",2,42,"Duchess Branch",32,6620,"N","N/A"]
[888,"1-34-9-22-W4",1,114,"Mainline East (West)",1,4960,"Y","N/A","2020-07-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[889,"16-24-52-23-W4M",3,406,"Viking 3 and 4",18,4960,"Y","2017-11-01","2018-08-01","Defects Found","N","N/A","2018-05-01","Repairs Required","N"]
[890," 10-28-45-28-W3M",1,610,"Homeglen Transmission",2,6200,"Y","N/A","2017-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[891," 3-1-49-13-W4M",2,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-08-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[892," 1-2-49-13-W4M",1,406,"Viking 3 and 4 Transmission",2,4960,"Y","N/A","2018-08-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[893," 1-4-49-13-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-08-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[894," 4-5-49-13-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[895," 2-6-49-13-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[896," 4-1-49-14-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[897," 4-1-49-14-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[898," 4-3-49-14-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[899," 2-5-49-14-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[900," 4-6-49-14-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[901," 2-1-49-15-W4M",1,406,"Viking 3 and 4 Transmission",2,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[902," 4-1-49-15-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-18","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[903," 3-3-49-15-W4M",1,406,"Viking 3 and 4 Transmission",14,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[904," 2-13-49-16-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[905,"10-08-56-21-W4M",1,114,"Swan Hills Transmission",8,6380,"Y","2018-09-01","2019-06-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[906,"02-02-49-14-W4M",1,406,"Viking 3 and 4 Transmission",2,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[907,"01-03-49-14-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[908,"02-03-49-14-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[909,"03-02-49-15-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[910,"13-07-49-15-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[911,"08-14-49-16-W4M",1,406,"Viking 3 and 4 Transmission",2,4960,"Y","N/A","2018-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[912,"04-04-49-13-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-10-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[913,"05-13-49-16-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-10-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[914,"16-20-49-16-W4M",1,406,"Viking 3 and 4 Transmission",14,4960,"Y","N/A","2018-10-18","Defects Found","N","N/A","2019-04-01","Repairs Required","Y"]
[915,"15-22-53-17-W5M",1,273,"Hinton-Wabamun Transmission",2,7240,"Y","N/A","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[916,"01-27-53-10-W5M",1,273,"Hinton-Wabamun Transmission",1,7240,"Y","N/A","2018-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[918,"03-14-55-22-W4M",2,114,"Bittern Lake to Redwater Transmission",5,4960,"Y","2018-10-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[919,"03-13-49-16-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2018-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[920,"01-05-49-13-W4M",1,406,"Viking 3 and 4 Transmission",8,4960,"Y","N/A","2019-01-01","Defects Found","N","N/A","2019-04-01","No Repairs Required","N/A"]
[921,"01-02-49-15-W4M",1,406,"Viking 3 and 4 Transmission",2,4960,"Y","N/A","2019-01-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[922,"15-31-94-10-W4M",2,114,"Fort McMurray Transmission",14,9930,"Y","2019-02-01","2019-02-01","Defects Found","N","N/A","2019-09-01","No Repairs Required","N/A"]
[923,"08-12-37-28-W4M",2,168,"Nevis-Airdrie",1,4960,"Y","N/A","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[924,"04-15-29-01-W5M",2,114,"Nevis-Airdrie",1,4960,"Y","N/A","2019-03-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[925,"03-16-19-14-W4M",2,60,"Brooks Lakeside Feeders Tr.Line",2,4970,"Y","2019-03-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[926,"08-28-48-26-W4M",2,60,"Millet Transmission",16,5510,"Y","N/A","2019-05-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[927,"03-16-48-25-W4M",2,60,"Millet Transmission",16,5510,"Y","N/A","2019-05-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[928,"09-09-48-25-W4M",2,60,"Millet Transmission",5,5510,"Y","N/A","2019-05-01","Defects Found","Y","N/A","Not Required","Repairs Required","Y"]
[929,"04-11-48-25-W4M",2,60,"Millet Transmission",5,5510,"Y","N/A","2019-05-01","Defects Found","Y","N/A","Not Required","Repairs Required","Y"]
[930,"12-01-48-25-W4M",2,60,"Millet Transmission",16,5510,"Y","N/A","2019-05-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[931,"03-01-48-25-W4M",2,60,"Millet Transmission",16,5510,"Y","N/A","2019-05-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[932,"01-01-48-25-W4M",2,60,"Millet Transmission",16,5510,"Y","N/A","2019-05-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[933,"LSD 13-34-37-27-W4M and LSD 04-29-37-27-W4M",2,168," Nevis-Airdrie Transmission",3,4960,"Y","N/A","2019-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[934,"LSD 04-02-38-27-W4M and LSD 16-21-38-27-W4M",2,168," Nevis-Airdrie Transmission",3,4960,"Y","N/A","2019-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[935,"8-5-55-22-W4M",2,273,"Bitttern Lake Transmission",2,6580,"Y","N/A","2019-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[936,"SE-01-53-24-W4M to NE-01-53-24-W4M",2,323,"CIL Transmission",11,3450,"Y","2019-07-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[937,"02-05-47-27-W4M",1,610,"Homeglen Transmission",2,6200,"Y","N/A","2019-07-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[938,"LSD 3-21-25-29-W4",2,323,"Jumping Pound Transmission",31,4960,"Y","2019-07-01","2020-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[939,"LSD 3-21-25-29-W4",2,323,"Jumping Pound Transmission",2,4960,"N","N/A"]
[940,"LSD 3-21-25-29-W4",2,323,"Jumping Pound Transmission",2,4960,"Y","N/A","2020-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[941,"12-30-24-02-W5M",2,168,"Valley Ridge Branch",8,4960,"Y","2019-07-01",null,"No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[942,"02-17-47-27-W4M",1,610,"Homeglen Transmission",2,6200,"Y","N/A","2019-09-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[943,"14-06-48-26-W4M",1,323,"Bonnie Glen Transmission",3,5520,"Y","N/A","2019-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[944,"01-02-53-01-W5M",2,60,"Stony Plain Transmission",2,3450,"Y","N/A","2019-12-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[945,"NW-27-038-01-W5 &\nNE-28-038-01-W5",3,168,"Sylvan Lake Transmission",3,4690,"Y","N/A","2021-03-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[946,"SE-34-38-01-W5M",1,168,"Sylvan Lake Transmission",2,4690,"Y","N/A","2021-06-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[947,"SE-34-38-01-W5M",1,168,"Sylvan Lake Transmission",4,4690,"Y","N/A","2021-01-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[948,"13-16-06-11-W4M",2,88,"Foremost Branch Line",1,4970,"Y","N/A","2021-10-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[950,"SE-35-51-23-W4M",1,88,"Bretona Transmission",2,4960,"Y","N/A","2020-10-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[951,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",7,4830,"Y","N/A","2020-06-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[952,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",5,4830,"Y","N/A","2020-04-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[953,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",7,4830,"Y","N/A","2020-04-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[954,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",9,4830,"Y","N/A","2020-09-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[955,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",7,4830,"Y","N/A","2020-05-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[956,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",11,4830,"Y","N/A","2021-02-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[957,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",9,4830,"Y","N/A","2020-05-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[958,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",3,4830,"Y","N/A","2020-05-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[959,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",3,4830,"Y","N/A","2020-11-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[960,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",3,4830,"Y","N/A","2020-04-20","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[961,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",3,4830,"Y","N/A","2020-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[962,"NE-22-46-22-W4 to SE-27-49-17-W4",1,168,"Southern Extension",7,4830,"Y","N/A","2020-04-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[963,"14-22-41-26-W4M",1,60,"Southern Extension",3,4830,"Y","N/A","2021-02-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[964,"04-35-41-26-W4M",1,60,"Southern Extension",3,4830,"Y","N/A","2020-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[965,"15-35-41-26-W4M",1,60,"Southern Extension",3,4830,"Y","N/A","2020-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[966,"09-13-42-26-W4M",1,60,"Southern Extension",4,4830,"Y","N/A","2020-04-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[967,"02-30-42-25-W4M",1,60,"Southern Extension",4,4830,"Y","N/A","2021-01-01","Defects Found","N","N/A","Not Started","Unknown","N"]
[968,"16-09-43-25-W4M",1,60,"Southern Extension",5,4830,"Y","N/A","2020-05-20","Defects Found","N","N/A","Not Started","Unknown","N"]
[969,"05-26-43-25-W4M",1,60,"Southern Extension",8,4830,"Y","N/A","2021-01-21","Defects Found","N","N/A","Not Started","Unknown","N"]
[970,"SE-19-46-22-W4M",1,60,"Southern Extension",14,4830,"N","N/A"]
[971,"10-02-35-05-W4M",1,42,"Monitor Lateral",2,5550,"Y","N/A","2020-02-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[972,"06-12-10-16-W4M",1,88,"Mainline East (East)",1,4960,"Y","N/A","2020-03-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[973,"E (1/2) 29-22-29-W4",3,219,"McKenzie Gate Lateral",6,6140,"Y","N/A","2020-06-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[974,"NE-09-053-22-W4",2,273,"Ardrossan Transmission",3,3100,"Y","2018-05-01","N/A","Defects Found","N","N/A","Not Required","N/A","N - Piping Removed"]
[975,"04-06-35-28-W4M",2,168,"Nevis-Airdrie",2,4960,"Y","N/A","2021-02-21","No Defects Found","N/A","N/A","N/A","N/A","N/A"]
[976,"01-28-50-09-W4",1,323,"Birch Lake Transmission",25,8450,"Y","2018-10-01","N/A","Defects Found","N","N/A","Not Started","Unknown","N"]
[977,"2-21-53-23-W4M",2,406,"Cloverbar Compressor",2,8450,"N",null,"N/A"]
[978,"10-08-56-21-W4M",1,323,"Inland Transmission",10,null,"N",null,"N/A"]
[979,"NW-28-37-27-W4",2,168,"Nevis-Airdrie",8,4960,"N","N/A"]
[980,"NW 25-34-01-W5M",1,168,"Nevis-Airdrie",2,4960,"N","N/A"]
[981,"12-33-40-26-W4M to 7-32-40-26-W4M",2,114,"Southern Extension",65,4830,"N","N/A"]
[982,"01-01-40-27-W4M to 04-01-40-27-W4M",2,114,"Southern Extension",73,4830,"N","N/A"]
[983,"13-21-40-26-W4M to 16-19-40-26-W4M",2,168,"Southern Extension",92,4830,"N","N/A"]
[984,"12-23-39-27-W4M",2,60,"Southern Extension",42,4830,"N","N/A"]
[985,"NW-27-053-25-W4 & \nNE-28-053-25-W4 &\nSE-02-052-25-W4",3,323,"Villeneuve Transmission",6,8480,"Y","N/A","2020-11-01","No Defects Found","N/A","N/A","N/A","N/A","N/A"]